Pressure test certificate for RAUTITAN pipe systems

1.	Project Data

Project:

Client:

Number / Street:

City / Postcode:

RAUTITAN system:	 platinum/his311	 red	 green	 lilac	 stabil

Location/Pipe section:

2. Preliminary Test

2.1 Test pressure 	         	 bar /  kPa (pressure 15 bar / 1500 kPa)

2.2 Current pressure after 10 min          	 bar /  kPa (restore test pressure)

2.3 Current pressure after 20 min          	 bar /  kPa (restore test pressure)

2.4 Current pressure after 30 min          	 bar /  kPa

2.5 Current pressure after 60 min          	 bar /  kPa (permissible pressure loss < 0.6 bar / < 60 kPa)

Entire installation has been checked visually for leaks including all joints and no leaks were found.

3. Main Test

3.1 Test pressure 	          	 bar /  kPa (result of the preliminary test as per Item 2.5)

3.2 Current pressure after 2 h 	          	 bar /  kPa (permissible pressure loss < 0.2 bar / < 20 kPa)

3.3 Comments:

Entire installation has been checked visually for leaks including all joints and no leaks were found.

The complete installation is free from leaks.

At no point in the installation must water leak from pipes or joints

4. Confirmation

The pressure test was performed as per above procedure. No leaks were present and no components permanently distorted.

Installer

Contractor 								Date (dd/mm/yyyy)