REHAU Specification Texts

RAUTITAN Plumbing and Gas systems

System	Page

RAUTITAN platinum – hot and cold water	 2

RAUTITAN red – hot water	 4

RAUTITAN green – rainwater	 6

RAUTITAN lilac – recycled water	 8

RAUTITAN pink – under floor heating and cooling, radiator heating	10

RAUTITAN stabil – hot and cold water, and heating and cooling	12

RAUTITAN gas stabil – gas	14

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN platinum

- GENERAL

This section relates to REHAU RAUTITAN plumbing system for hot and cold water installation, from the network utility supply authority water main to designated points and appliances.

- System description

The REHAU RAUTITAN platinum plumbing system for hot and cold water applications of 16 to 63mm consists of:

- RAUTITAN platinum pipe

- PX fittings and sleeves

- MX fittings and sleeves

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 3500	Plumbing and drainage set

AS/NZS 2492	Cross-linked polyethylene (PE-X) pipes for pressure applications

AS/NZS 2537	Mechanical jointing fittings for use with cross-linked polyethylene (PE-X) pipe for hot and cold water applications

AS/NZS 4020	Testing of products for use in contact with drinking water

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 3500.1	Plumbing and drainage – Part 1: Water Services

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- MATERIALS

## Pipe materials

Pipe materials shall be PE-Xa/PE construction, consisting of PE-Xa inner layer and a PE outer marking layer, certified to AS/NZS 2492 for water service applications.

Suitable for use in hot and cold water applications in buildings in accordance with AS/NZS 3500.

## Pipe performance specification

| Product | RAUTITAN platinum |
| --- | --- |
| Colour | Platinum (dark silver-grey) |
| Material | Flexible, high-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892/16893) |
| Pressure rating | PN20 (in accordance with AS/NZS 2492) |
| Design pressure | A Class.1-5/10bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 90 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16 x 2.2mm 40 x 5.5mm 20 x 2.8mm 50 x 6.9mm 25 x 3.5mm 63 x 8.6mm 32 x 4.4mm |
| Australia and New Zealand approvals and certifications | AS/NZS 2492:2007 AS/NZS 4020 BRANZ appraisal no. 434 Watermark licence number LN01413 |

Pipe sizes 16mm and 20mm also available as pre-insulated pipe R=0.3 with outer PE insulation foam, with tear-resistant and moisture-blocking outer layer, for protection against heat loss in hot water pipes, condensation and heating of cold water pipes and as a sound insulation when installed in concealed location.

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX or MX, Watermark approved and certified to AS/NZS 2537.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16-40mm.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16-40mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-63mm threaded connections and 50-63mm threadless connections.

RAUTITAN MX sleeves made of thermally annealed brass, manufactured in accordance with DIN EN 12164, DIN EN 12165 and DIN EN 12168, shall be used for connections 50-63mm.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturer’s standard form.

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN red

- GENERAL

This section relates to REHAU RAUTITAN plumbing system for hot installation, from the network utility supply authority water main to designated points and appliances.

- System description

The REHAU RAUTITAN red plumbing system for hot water applications of 16 to 25mm consists of:

- RAUTITAN red pipe

- PX fittings and sleeves

- threaded MX fittings

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 3500	Plumbing and drainage set

AS/NZS 2492	Cross-linked polyethylene (PE-X) pipes for pressure applications

AS/NZS 2537	Mechanical jointing fittings for use with cross-linked polyethylene (PE-X) pipe for hot and cold water applications

AS/NZS 4020	Testing of products for use in contact with drinking water

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 3500.1	Plumbing and drainage – Part 1: Water Services

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- MATERIALS

## Pipe materials

Pipe materials shall be PE-Xa/PE construction, consisting of PE-Xa inner layer and a PE outer marking layer, certified to AS/NZS 2492 for water service applications.

Suitable for use in hot water applications in buildings in accordance with AS/NZS 3500.

## Pipe performance specification

| Product | RAUTITAN red |
| --- | --- |
| Colour | Red |
| Material | Flexible, high-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892/16893) |
| Pressure rating | PN20 (in accordance with AS/NZS 2492) |
| Design pressure | A Class.1-5/10bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 90 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16 x 2.2mm 20 x 2.8mm 25 x 3.5mm |
| Australia and New Zealand approvals and certifications | AS/NZS 2492:2007 AS/NZS 4020 BRANZ appraisal no. 434 Watermark licence number LN01413 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX, Watermark approved and certified to AS/NZS 2537.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16-25mm.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16-25mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-25mm threaded connections.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturer’s standard form.

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN green

- GENERAL

This section relates to REHAU RAUTITAN rainwater supply system, from the rainwater storage tank to designated points and appliances.

- System description

The REHAU RAUTITAN green plumbing system for rainwater applications of 16 to 63mm consists of:

- RAUTITAN green pipe

- PX fittings and sleeves

- threaded MX fittings

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 3500	Plumbing and drainage set

AS/NZS 2492	Cross-linked polyethylene (PE-X) pipes for pressure applications

AS/NZS 2537	Mechanical jointing fittings for use with cross-linked polyethylene (PE-X) pipe for hot and cold water applications

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone:	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 3500.1	Plumbing and drainage – Part 1: Water Services

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- Materials

## Pipe materials

Pipe materials shall be PE-Xa/PE construction, consisting of PE-Xa inner layer, a black PE middle layer and a PE outer marking layer, certified to AS/NZS 2492 for water service applications.

Suitable for use in rainwater applications in buildings in accordance with AS/NZS 3500.

## Pipe performance specification

| Product | RAUTITAN green |
| --- | --- |
| Colour | green |
| Marking (each meter of pipe length) | “Rainwater” |
| Material | Flexible, high-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892/16893) |
| Pressure rating | PN20 (in accordance with AS/NZS 2492) |
| Design pressure | A Class.1-5/8bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 90 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16 x 2.2mm 40 x 5.5mm 20 x 2.8mm 50 x 6.9mm 25 x 3.5mm 63 x 8.6mm 32 x 4.4mm |
| Australia and New Zealand approvals and certifications | AS/NZS 2492:2007 BRANZ appraisal no. 434 Watermark licence number LN01413 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX or MX, Watermark approved and certified to AS/NZS 2537.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16-40mm.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16-40mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-63mm threaded connections and 50-63mm threadless connections.

RAUTITAN MX sleeves made of thermally annealed brass, manufactured in accordance with DIN EN 12164, DIN EN 12165 and DIN EN 12168, shall be used for connections 50-63mm.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturer’s standard form.

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN lilac

- GENERAL

This section relates to REHAU RAUTITAN recycled water supply system, from the network utility supply authority recycled water main to designated points and appliances.

- System description

The REHAU RAUTITAN lilac plumbing system for recycled water applications of 16 to 63mm consists of:

- RAUTITAN lilac pipe

- PX fittings and sleeves

- threaded MX fittings

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 3500	Plumbing and drainage set

AS/NZS 2492	Cross-linked polyethylene (PE-X) pipes for pressure applications

AS/NZS 2537	Mechanical jointing fittings for use with cross-linked polyethylene (PE-X) pipe for hot and cold water applications

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 3500.1	Plumbing and drainage – Part 1: Water Services

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- Materials

## Pipe materials

Pipe materials shall be PE-Xa/PE construction, consisting of PE-Xa inner layer and a PE outer marking layer, certified to AS/NZS 2492 for water service applications.

Suitable for use in recycled water applications in buildings in accordance with AS/NZS 3500.

## Pipe performance specification

| Product | RAUTITAN lilac |
| --- | --- |
| Colour | lilac |
| Marking (each meter of pipe length) | “Recycled or reclaimed water – do not drink” |
| Material | Flexible, high-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892/16893) |
| Pressure rating | PN20 (in accordance with AS/NZS 2492) |
| Design pressure | A Class.1-5/10bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 90 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16 x 2.2mm 40 x 5.5mm 20 x 2.8mm 50 x 6.9mm 25 x 3.5mm 63 x 8.6mm 32 x 4.4mm |
| Australia and New Zealand approvals and certifications | AS/NZS 2492:2007 BRANZ appraisal no. 434 Watermark licence number LN01413 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX or MX, Watermark approved and certified to AS/NZS 2537.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16-40mm.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16-40mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-63mm threaded connections and 50-63mm threadless connections.

RAUTITAN MX sleeves made of thermally annealed brass, manufactured in accordance with DIN EN 12164, DIN EN 12165 and DIN EN 12168, shall be used for connections 50-63mm.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturers standard form.

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN pink

- GENERAL

This section relates to REHAU RAUTITAN Under Floor Heating / Cooling system.

- System description

The REHAU RAUTITAN system for under floor heating and cooling applications of 16 to 40mm consists of:

- RAUTITAN pink pipe

- PX fittings and sleeves

- threaded MX fittings

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

BS EN 1264 	Floor heating - Systems and components

BS EN 13163 	Thermal insulation products for buildings. Factory made products of expanded polystyrene. Specification

BS 7291 	Thermoplastic pipes and associated fittings for hot and cold water for domestic purposes and heating installations in buildings

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU Piping, Connection and System Guidelines – Technical information

REHAU Under Floor Heating/Cooling – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design, installation and commissioning

Planning, installation and commissioning must comply with the following documents:

BS EN 1264 	Floor heating - Systems and components

REHAU Piping, Connection and System Guidelines – Technical information

REHAU Under Floor Heating/Cooling – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- MATERIALS

## Pipe materials

Pipe materials shall be PE-Xa/PE construction, consisting of PE-Xa inner layer, an EVOH oxygen barrier, and a PE outer marking layer.

Suitable for use in heating and cooling applications in residential and commercial applications in accordance with BS EN 1264 and BS 7291.

## Pipe performance specification

| Product | RAUTITAN pink |
| --- | --- |
| Colour | Pink |
| Material | Flexible, high-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892/16893) |
| Pressure rating | PN20 (in accordance with AS/NZS 2492) |
| Design pressure | A Class.1-5/10bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 90 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16 x 2.2mm 32 x 4.4mm 20 x 2.8mm 40 x 5.5mm 25 x 3.5mm |
| Australia and New Zealand approvals and certifications | AS/NZS 2492:2007 BRANZ appraisal no. 434 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX or MX, Watermark approved and certified to AS/NZS 2537.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16 to 40mm. Protected by Australian Design Registration No. 327395, 327396 and 327397.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16 to 40mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all threaded connections from 16 to 40mm.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturers standard form.

Technical specification – REHAU RAUTITAN Plumbing System

RAUTITAN stabil

- GENERAL

This section relates to REHAU RAUTITAN plumbing system for hot and cold water installation, from the network utility supply authority water main to designated points and appliances, and Under Floor Heating and Cooling.

- System description

The REHAU RAUTITAN stabil plumbing system for hot and cold water, and heating and cooling applications of 16 to 40mm consists of:

- RAUTITAN stabil pipe

- PX fittings and sleeves

- threaded MX fittings

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 3500	Plumbing and drainage set

AS 4176	Multilayer pipe system for pressure applications

AS/NZS 2537	Mechanical jointing fittings for use with cross-linked polyethylene (PE-X) pipe for hot and cold water applications

AS/NZS 4020	Testing of products for use in contact with drinking water

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 3500.1	Plumbing and drainage – Part 1: Water Services

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Water Service – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- MATERIALS

## Pipe materials

Pipes shall be of composite construction, certified to AS 4176 respectively ATS5200.490 for pressure applications, consisting of PE-Xa inner layer, an aluminium oxygen barrier, and a PE outer marking layer.

Suitable for use in hot and cold water applications in buildings in accordance with AS/NZS 3500.

## Pipe performance specification

| Product | RAUTITAN stabil |
| --- | --- |
| Colour | Silver |
| Material | High-pressure cross-linked polyethylene pipe PE-Xa inliner (in accordance with DIN 16892), Aluminium |
| Pressure rating | PN20 (based on AS/NZS 2492) |
| Design pressure | A Class.1-5/10bar (in accordance with ISO 15875) |
| Continuous operation | 70 °C at 1,000 kPa |
| Maximum operating temperature | 95 °C |
| short-term maximum temperature | 100 °C |
| Operational life time (at 70°C / 1,000 kPa) | 50 years |
| Available sizes in mm | 16.2 x 2.6mm 32 x 4.7mm 20 x 2.9mm 40 x 6.0mm 25 x 3.7mm |
| Australia and New Zealand approvals and certifications | AS 4176 / ATS 5200.490 AS/NZS 4020 BRANZ appraisal no. 434 Watermark licence number LN21210 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Approved for flush-mounted installation

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN PX or MX, Watermark approved and certified.

RAUTITAN PX Polymer fittings made of PPSU (colour: black) with tool tabs for precise attachment of the assembly tool RAUTOOL shall be used for threadless connections from 16-40mm.

RAUTITAN PX multi directional polymer sleeves made of PVDF (colour: black) with laser engraved production date shall be used for all connections from 16-40mm.

RAUTITAN MX DZR Brass fittings made of special dezincification-resistant brass, manufactured in accordance with AS2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-40mm threaded connections.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturer’s standard form.

Technical specification – REHAU RAUTITAN Gas System

RAUTITAN gas stabil

- GENERAL

This section relates to REHAU RAUTITAN gas system for NG and LPG installation, downstream of the point of supply (as defined in AS/NZS 5601.1 - Section 1) to designated points and appliances.

- System description

The REHAU RAUTITAN gas stabil system for gas applications of 16 to 40mm consists of:

- RAUTITAN gas stabil pipe

- RAUTITAN gas fittings and sleeves

- Reference documentation

The documents referred to in this section are:

NCC / BCA	Building Code of Australia

AS/NZS 5601.1	Gas installations

AS 4176.8	Multilayer pipes for pressure applications

## Manufacturers documentation

Manufacturer’s and supplier’s documents relating to work in this section are:

REHAU RAUTITAN – Water, Gas & Heating Product book

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN – Gas Installation System – Technical Information

The above information is available from REHAU:

Web:	www.rehau.com.au

Phone: 	1300 768 033 (Australia only) or +61 2 8741 4500

- General system design and performance

Planning, installation and commissioning must comply with the following documents:

AS/NZS 5601.1	Gas Installation – Part 1: General Installations

REHAU Piping, Connection and System Guidelines – Technical information

RAUTITAN gas Installation System – Technical Information

Installers to be a member of the REHAU Authorised Installer Network RAIN, familiar with the materials and the techniques specified.

- MATERIALS

## Pipe materials

Pipes shall be of composite construction, certified to AS4176.8 for pressure applications, consisting of PE-Xa inner layer, an aluminium oxygen barrier, and a PE outer marking layer.

## Pipe performance specification

| Product | RAUTITAN gas stabil |
| --- | --- |
| Colour | Yellow |
| Material | High-pressure cross-linked polyethylene pipe PE-Xa (in accordance with DIN 16892), Aluminium |
| Continuous operating temperature | 60 °C |
| short-term maximum temperature | 90 °C |
| Continuous operating pressure | 70 kPa |
| Minimum designed service life | 50 years |
| Available sizes in mm | 16.2 x 2.6mm 25 x 3.7mm 20 x 2.9mm 32 x 4.7mm 40 x 6.0mm |
| Approvals and certifications | AS 4176.8-2010 |

## Connection – compression fittings and sleeves

Connections shall be axial compression sleeve mechanism, featuring the following benefits:

- Permanently sealing compression sleeve jointing technique

- Self-sealing pipe material – connection without the use of an O-ring

- Increased hydraulic properties based on expansion technology

- Robust jointing technique highly suitable for construction sites.

- Simple visual inspection

- Joint can be pressurised immediately after installation.

- Requires no calibration or deburring

- Same jointing technique and tools for water services, gas and heating installation

Fittings and sleeves shall be REHAU RAUTITAN gas with yellow dot, approved and certified to AS 4176.8. Each fitting packed with the adjacent sleeves as one set into a bag.

RAUTITAN gas DZR Brass fittings with yellow dot, made of special dezincification-resistant brass, manufactured in accordance with AS 2345, DIN EN 12164, DIN EN 12165 and DIN EN 12168 grade A (equivalent to highest requirement category), shall be used for all 16-40mm connections.

RAUTITAN gas sleeves with yellow dot, made of thermally annealed brass, manufactured in accordance with DIN EN 12164, DIN EN 12165 and DIN EN 12168, shall be used for connections 16-40mm.

- Manufacturer Warranty

Warranty period: 	25 years

From: 	Date of completion of system testing.

For Terms and Conditions see REHAU RAUTITAN Warranty Certificate in the manufacturer’s standard form.