## Information
Go to selection tool
For a visual explanation of how this tool works, please see our 'how-to' tutorial video.
Louvre codes take the form 1UL/S where the first number is the number of louvre banks (1, 2 or 3)
1 | and the final letter denotes whether the lovre is shallow section 50mm pitch (S) or deep section 100mm pitch (D).
The louvre performance data is taken from BSRIA report number 55130/1 dated December 1988.
2
Louvre air flow performance was measured with birdguard fitted.
3 | Percent change in Cv is taken as:
|  | No b.g. | With i.m.
| 1UL | 7 | -6
| 2UL | 4 | -4
| 3UL | 3 | -3
The louvre weights are for the louvre, mullions and frame and exclude any support steelwork.
4
The classifications for 'location' are taken from CIBSE Guide A, 3.3.9.4
5 | sheltered is up to 3rd floor in city centres
normal is 4th to 8th floors in city centres and most rural and suburban buildings
severe is 9th floor and above in city centres, floors above 5th in rural and suburban areas and coastal and hill sites.
Steelwork spacing should be as calculated from the design charts in GPTS 1200 or Colt leaflets.
6 | The default values used are typical values for' normal' locations.
Classifications are taken from BS EN 13030 (formerly the HEVAC test method).
7
A = 99% rainfall rejection or better
B = 95% to 98.99% rainfall rejection
C = 80% to 94.99% rainfall rejection
D = less than 80% rainfall rejection
1 = Airflow coefficient (Cv) of 0.4 or better
2 = Airflow coefficient (Cv) of 0.3 to 0.399
3 = Airflow coeficient (Cv) of 0.2 to 0.299
4 = Airflow coefficient (Cv) of less than 0.2
Core velocity is the nominal velocity through the louvre panel ignoring the blockage effect of the louvres themselves.
8
Where other equipment in series is selected the program assumes a useful throat area equivalent to the louvre core area.
9 | This is intended to provide a conservative selection.
The easiest way to copy into Word for a report is to highlight and copy, then go to the Word document and click on
10 | edit, paste special, picture. The text is not editable but is correctly laid out and can be moved and resized.

## Data input and results
UNIVERSAL LOUVRE SELECTION
PROJECT:
DATE: |  |  |  | BY:
INPUT DATA:
Louvre type |  |  | Material
Not in use
Not in use |  |  | Mullion spacing |  |  |  | m
Accessories |  |  | Steelwork |  | 1UL |  | m
|  |  | spacing |  | 2UL |  | m
Direction of air flow |  |  |  |  | 3UL |  | m
Connections |  |  | Steelwork thickness |  |  |  | m
Air flow rate |  | m3/s | Ambient air density |  |  |  | kg/m3
Other equipment in series |  |  | Not in use
Not in use
Maximum air pressure drop |  | Pa
Fill in 2 out of 3
Maximum louvre height |  | m | Leave 3rd blank
Maximum louvre width |  | m
RESULTS |  | Option 1 |  |  | Option 2
|  | (Best weather protection) |  |  | (Best air flow performance)
Selected louvre type |  | N/A |  |  | N/A
HEVAC classification |  | N/A |  |  | N/A
Pressure drop |  | N/A | Pa |  | N/A | Pa
Core velocity |  | N/A | m/s |  | N/A | m/s
Panel height |  | N/A | m |  | N/A | m
Panel width |  | N/A | m |  | N/A | m
Panel weight |  | N/A | kg |  | N/A | kg
Copyright Colt International Limited 2013 |  |  |  |  | v1.1pub May 2013

## selection (hidden)
Table of choices
Weather resistance | critical | important | unimportant |  | critical | important | unimportant |  | critical | important | unimportant
location | exposed | exposed | exposed |  | normal | normal | normal |  | sheltered | sheltered | sheltered
choice 1 | 3UL | 3UL | 1UL |  | 3UL | 2UL | 1UL |  | 3UL | 2UL | 1UL
choice 2 | N/A | 2UL | N/A |  | 2UL | N/A | N/A |  | 2UL | N/A | N/A
[10 empty] | al | al | ss | ss | gs | gs
Choice from table: | choice 1 | 1UL | [6 empty] | 1UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| choice 2 | N/A | [6 empty] | 1UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | core velocity |  |  |  | weight | 2UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Louvre type: | choice 1 | N/A |  | 0 |  |  |  |  | 2UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| choice 2 | N/A |  | 0 |  |  |  |  | 3UL/D | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | 3UL/S | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
RESULTS |  |  | Option 1 |  |  | Option 2
|  |  | (Best weather protection) |  |  | (Best air flow performance)
Selected louvre type |  |  | N/A |  |  | N/A
HEVAC classification |  |  | N/A |  |  | N/A
Pressure drop |  |  | N/A | Pa |  | N/A | Pa
Core Velocity |  |  | N/A | m/s |  | N/A | m/s
Panel height |  |  | N/A | m |  | N/A | m
Panel width |  |  | N/A | m |  | N/A | m
Percentage free area |  |  | #VALUE! |  |  | N/A
Measured free area |  |  | #VALUE! | m2 |  | N/A | m2
Weight |  |  | N/A | kg |  | N/A | kg

## ulpanel (hidden)
Calculations:
if height entered....
[10 empty] | zeta | accfac | cvel | carea | cwidth | nummull | oawid
Colt Universal Louvre Systems | [8 empty] | 1 | 5.29 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Calculation of Panel Size if Flowrate and Maximum Pressure Drop are known | [8 empty] | 2 | 6.93 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 3 | 4.29 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 4 | 6.43 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Input Data: | [8 empty] | 5 | 4.53 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 6 | 4.72 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Volume flow rate: | [5 empty] | 0 | m3/s |  | 7 | 3.53 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Maximum Pressure Drop: | [5 empty] | 0 | Pa |  | 8 | 4.22 | 0.94 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Mullion spacing: | [5 empty] | 1 | m |  | 9 | 10.54 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Site ambient air density: | [5 empty] | 1.2 | kg/m3 |  | 10 | 16 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 11 | 9.54 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 12 | 15.5 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Limiting Dimension: |  |  |  |  | h or w | w |  |  | 13 | 14.79 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
(h = height, w = width) |  |  |  |  | value | 0 | m |  | 14 | 16 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[5 empty] | 1UL | 2UL | 3UL |  | 15 | 13.79 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Thickness of horizontal steelwork: |  |  |  |  | 0.1 | 0.1 | 0.1 | m | 16 | 15.5 | 0.96 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Spacing of horizontal steelwork: |  |  |  |  | 1.25 | 2 | 3.2 | m | 17 | 13.03 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Calculations: | [8 empty] | 18 | 20.66 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Width (m) | Height (m) |  | Value for selection |  | cvel | 19 | 12.03 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | 20 | 20.16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1UL/SH: |  | inlet | 0 | #DIV/0! |  | 1UL/D | #DIV/0! | 0 | 21 | 16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  | 1UL/S | #DIV/0! | 0 | 22 | 20.66 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
1UL/DH: |  | inlet | 0 | #DIV/0! |  | 2UL/D | #DIV/0! | 0 | 23 | 15 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  | 2UL/S | #DIV/0! | 0 | 24 | 20.16 | 0.97 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2UL/SH: |  | inlet | 0 | #DIV/0! |  | 3UL/D | #DIV/0! | 0 |  | if width entered....
|  | exhaust | 0 | #DIV/0! |  | 3UL/S | #DIV/0! | 0 |  | nummull | cwidth | cheight | oaht
2UL/DH: |  | inlet | 0 | #DIV/0! |  |  |  |  | 1 | 0 | -0.18 | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 2 | 0 | -0.18 | #DIV/0! | #DIV/0!
3UL/SH: |  | inlet | 0 | #DIV/0! |  |  |  |  | 3 | 0 | -0.18 | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 4 | 0 | -0.18 | #DIV/0! | #DIV/0!
3UL/DH: |  | inlet | 0 | #DIV/0! |  |  |  |  | 5 | 0 | -0.18 | #DIV/0! | #DIV/0!
|  | exhaust | 0 | #DIV/0! |  |  |  |  | 6 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 7 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 8 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 9 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 10 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 11 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 12 | 0 | -0.18 | #DIV/0! | #DIV/0!
Notes: | [8 empty] | 13 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 14 | 0 | -0.18 | #DIV/0! | #DIV/0!
a) Pressure drops are based upon the following values of Cv: | [8 empty] | 15 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 16 | 0 | -0.18 | #DIV/0! | #DIV/0!
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract | 17 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/SH: | 0.435 | 0.38 | 2UL/SH: | 0.308 | 0.25 | 3UL/SH: | 0.277 | 0.22 | 18 | 0 | -0.18 | #DIV/0! | #DIV/0!
1UL/DH: | 0.47 | 0.46 | 2UL/DH: | 0.26 | 0.25 | 3UL/DH: | 0.25 | 0.22 | 19 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 20 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 21 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 22 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 23 | 0 | -0.18 | #DIV/0! | #DIV/0!
[9 empty] | 24 | 0 | -0.18 | #DIV/0! | #DIV/0!

## ulpress (hidden)
Calculations:
[10 empty] | zeta | accfac | nummull | cwidth | cheight | carea | cvel
Colt Universal Louvre Systems | [8 empty] | 1 | 5.29 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Calculation of Pressure Drop if Flowrate and Panel Size are known | [8 empty] | 2 | 6.93 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
(Louvre panels fitted with birdguard) | [8 empty] | 3 | 4.29 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 4 | 6.43 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Input Data: | [8 empty] | 5 | 4.53 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 6 | 4.72 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Volume flow rate: | [5 empty] | 0 | m3/s |  | 7 | 3.53 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Total panel width: | [5 empty] | 0 | m |  | 8 | 4.22 | 0.94 | 0 | -0.18 | -0.08 | 0.0144 | 0
Mullion spacing: | [5 empty] | 1 | m |  | 9 | 10.54 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Total panel height: | [5 empty] | 0 | m |  | 10 | 16 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[5 empty] | 1UL | 2UL | 3UL |  | 11 | 9.54 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Thickness of intermediate steelwork: |  |  |  |  | 0.1 | 0.1 | 0.1 | m | 12 | 15.5 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Spacing of intermediate steelwork: |  |  |  |  | 1.25 | 2 | 3.2 | m | 13 | 14.79 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
Site ambient air density: | [5 empty] | 1.2 | kg/m3 |  | 14 | 16 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 15 | 13.79 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 16 | 15.5 | 0.96 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 17 | 13.03 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 18 | 20.66 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
Calculations: | [8 empty] | 19 | 12.03 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 20 | 20.16 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
Pressure Drop: |  | Inlet | Extract |  | Value for selection |  | cvel |  | 21 | 16 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
[9 empty] | 22 | 20.66 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 1UL/D | 0 | 0 | Pa | 0 | Pa | 0 |  | 23 | 15 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 1UL/S | 0 | 0 | Pa | 0 | Pa | 0 |  | 24 | 20.16 | 0.97 | 0 | -0.18 | -0.08 | 0.0144 | 0
| 2UL/D | 0 | 0 | Pa | 0 | Pa | 0
| 2UL/S | 0 | 0 | Pa | 0 | Pa | 0
| 3UL/D | 0 | 0 | Pa | 0 | Pa | 0
| 3UL/S | 0 | 0 | Pa | 0 | Pa | 0
Notes:
a) Pressure drops are based upon the following values of Cv:
| Inlet | Extract |  | Inlet | Extract |  | Inlet | Extract
1UL/SH: | 0.435 | 0.38 | 2UL/SH: | 0.308 | 0.25 | 3UL/SH: | 0.277 | 0.22
1UL/DH: | 0.47 | 0.46 | 2UL/DH: | 0.26 | 0.25 | 3UL/DH: | 0.25 | 0.22